## User Guide - Read Me
Whole Home Sizing Worksheet
Version 1.1.2
Worksheet Purpose/Use:
The Generac PWRcell Whole Home Sizing Worksheet is designed based on NEC requirements in Part III of Article 220 and covers the sizing requirements for feeders suppling a residential dwelling unit. NOTE: NEC Article 702.4(B)(2) requires that the calculation of load on the optional standby source, which for the purposes of this worksheet is the PWRcell System, to be in accordance with the requirements in Article 220.
Worksheet Instructions:
The following instructions are provided to guide the user on how to properly fill out the Generac PWRcell Residential Whole Home Sizing Worksheet. It is the responsibility of the user to fill in the proper quantities and, where applicable, load information to the best of their knowledge and ability. NOTE: Within the instructions, key terms and section numbers are BLACK. User-entered values are BLUE. NEC references are in PURPLE. Instructions are sorted by the corresponding section number on the worksheet. Section numbers are ORANGE in color with paranthesis ["()"] surrounding the section number itself.
Section # | Instructions
(1) | General Loads include General Lighting Loads, Fixed Appliances, and Heat and A/C Loads.
(1a) | General Lighting Loads are defined as follows... 1. General Lighting and Receptacles: Calculated 3VA per square foot (sq. ft.). Enter in the home's square footage. This calculates the load for all lighting and general use receptacles. 2. Small Appliance Circuits: These are 20 A circuits for kitchen counter top and dining area receptacles. These circuits include refridgerators and freezers. Each circuit is calculated at 1500 VA. Enter in the total number of these circuits. NOTE: A minimum of two small appliance circuits are required to be entered. 3. Laundry Circuit: This circuit is calculated at 1500 VA. A minimum of one circuit is required to be entered. Washer and Gas Dryer units are connected to the laundry circuit.
(1b) | Per NEC Table 220.42, total Adjusted Lighting Load is calculated at 100% of the first 3000 VA of the cumulative total of unmanaged lighting load and 35% of that unmanaged load above 3000 VA.
(1c) | Fixed Appliances are appliances that are fastened in-place. Enter the quantity of these loads in the "Quantity" field. In most cases, a quantity of "1" will be entered. If the dwelling does not have a listed appliance, leave the field blank. Do NOT include Gas Appliances. Do NOT include non-fixed--in-place appliances such as Refridgerators or Freezers. All 240 V electric appliances have the option to be managed or locked out. This is done in practice using a Generac Smart Management Modules (SMMs) as part of the load management system. The use of load management is highly recommend for system operations. Large loads may also be completed locked out with SMMs. For more information about Load Management, see instructions for Section 4.
(1d) | Other Appliance Loads should include other fixed appliances that were not captured in Section 1c. 240 V loads entered into this section may opt to use load management. 120 V loads entered into this section may not opt to utilize load management. EXCEPTION: A 240 V subpanel where these 120 V loads are connected may an utilize an appropriately rated load management device to manage the entire subpanel.
(1e) | Per NEC Section 220.53, the total Adjusted Fixed Appliance Load is calculated depending on the number of connected and unmanaged fixed appliances. For dwellings with 3 or less unmanaged fixed appliances, 100% of the cumulative total of unmanaged fixed appliance load is applied. For dwellings with 4 or more unmanaged fixed appliances, 75% of the cumulative total of unmanaged fixed appliance load is applied.
(1f) | Per NEC Section 220.53, there are two types of Specifically-Adjusted Appliances (excluding heating or air-conditioning equipment covered in Section 2) that have their load ratings derived unique to fixed appliance loads. These loads are the Electric Clothes Dryer and Electric Cooking Appliances which are covered by NEC Section 220.54 and Section 220.55, respectively. Electric Clothes Dryer load rating is calculated as the greater of two values: 1) The load rating of the equipment or 2) 5000 VA. In other words, the Electric Clothes Dryer load is either 5000 VA or the nameplate ratings, whichever is higher. Electric Cooking Appliances (ex. Electric Range, counter-mounted cooktop, etc.) is calculated depending on the number of relavent appliances. For calculations in this worksheet, NEC Table 220.55 Column C is used. Therefore, it is assumed that the individual nameplate rating of any appliances covered under section are less than 12000 VA and are 240 V units. For calculations including loads individually greater than 12000 VA and/or single-phase units, please refer to NEC Section 220.55.
(2) | Heat and A/C Loads section has three main considerations: 1) A/C & Heat Pumps, 2) Supplimental Electric Heat, and 3) Fixed Electric Space Heating. Fill in the information for the equipment that is present in the dwelling. It is highly recommended that all Heat and A/C loads be connected to the load management system. A/C and Heat Pumps can be managed with the circuits inside the PWRcell ATS via its Controller board (a.k.a. the Smart A/C Control Management [SACM] board in other Generac ATSs). All other 240 V electric heating loads should be connected to appropriately sized Generac SMMs. Motor starting capabilities for these Heat and HVAC Loads must be taken into consideration as well. For more information, see instructions for Section 5. The maximum rated motor starting capability of a fully loaded PWRcell Battery is 50 A. Any demand seen from loads for a value above 50 A cannot and will not be achievable via the PWRcell Battery. Soft Starters are highly recommended for HVAC equipment to lower the required in-rush current (a.k.a surge current) for motor starting. Please consider baseloading in addition to the LRA values provided as they contribute to the maximum required current. A recommended soft starter is the Sure Start by Hyper Engineering. For A/Cs and Heat Pumps rated 3 tons or less, the use of a soft starter will ensure the PWRcell system can start the equipment. For A/C and Heat Pumps rated greater than 3 tons, it is recommended to enter the actual locked rotor amps (LRA) from the equipment dataplate into the corresponding field in Section 5.
(2a) | For A/C units & Heat Pumps, enter the number of units based on the tonnage of the unit. Equipment rated between whole tonnages should always be rounded up to the next highest tonnage. Ex. A 2.5 ton A/C unit should be entered in as a 3 ton A/C unit.
(2b) | For Supplimental Electric Heat (electric heat strips), enter the quantity as a count in increments of 5 kVA. Ex. 12.5 kW worth of electric heat strips should be entered as a quantity of 2.5.
(2c) | For Electric Heating, enter in the total feet of baseboard heat in the quantity field. Fixed electric space heating is estimated at 250 watts per foot.
(3) | The total NEC Calculated Load value is the combined total of all unmanaged load. It assumes a worst case scenario which does not necessarily dictate the actual load demand on the PWRcell system while in island mode. The color coding (green or red) of this cell reflects whether the NEC Calulated Load can be supported continuously by the PWRcell system. This is determined based on the maximum continuous AC power specification of the system. This is determined based the number of battery modules selected Section 7. In the event that the NEC Calculated Load exceeds PWRcell system capabilities based on selected made in Section 7, the NEC Calculated Load value will read "TOO HIGH". If this occurs, either more battery modules must be utilized OR more unmanaged load must be managed. NOTE: Total phase imbalance of loads being supported by the inverter during an outage (islanding) must not exceed 30%.
(4) | Managed and Locked Out Loads are loads that were selected to be connected to the load management system. These loads will appear in the list in Section 4. A Managed or Locked Out Load is required to be connected to either a PWRcell ATS Controller board (known as the Smart A/C Control Management [SACM] board inside other Generac ATSs) or an appropriately rated Generac SMM. Managed loads will only be energized if the inverter has the capability to energize the load. Managed loads may or may not be energized during a power outage depending on the load profile on the inverter. Managed loads will shed initilly upon power outage. The inverter also has the capability to control it's backup output power sent to the connected loads in a power outage should the connected loads exceed the inverter's capabilities as the PWRcell Battery is discharged. A/C and Heat Pumps can be managed with the Controller board inside the PWRcell ATS (known as the Smart A/C Control Management board in other Generac ATSs). All other 240 V electric heating loads should be connected to appropriately sized Generac SMMs. A Generac SMM is designed for the load management or load lockout of 240 VAC loads. Load management for 120 VAC loads is possible with a subpanel for 120 V loads managed by SMMs. The "Priority" setting of the SMM determines the order in which the manged loads are re-energized following an overload condition, with Priority 1 loads being first to energize and Priority 8 loads being last to energize. Where more than 4 SMM's are required, it is recommended to use the 100 A SMM to manage an entire subpanel. SMMs that are set to LOCK OUT will not allow the connected load to be energized while the PWRcell inverter is in island mode during a power outage.
(5) | The maximum rated motor starting capability of a fully populated PWRcell Battery is 50 A. Any demand seen from loads for a value above 50 A cannot and will not be achievable via the PWRcell System. Soft Starters are highly recommended for HVAC equipment to lower the required in-rush current (a.k.a surge current) for motor starting. Recommended soft starters are the Sure Start devices made by Hyper Engineering. Please consider baseload in addition to LRA for their contribution to max. required starting current. For A/Cs and Heat Pumps rated 3 tons or less, the use of a soft starter will ensure the PWRcell system can start the equipment. For A/C and Heat Pumps rated greater than 3 tons, it is recommended to enter the actual locked rotor amps (LRA) from the equipment dataplate into the "Actual Nameplate LRA" field in Section 5. The resulting value of "With Soft Starter" fields assume the use of a Sure Start product by Hyper Engineering and the manufacturer cited highest possible LRA suppression value of 60%.
(6) | The Estimated Continuous Load value is the estimated continuous load expected on the inverter based the total NEC Calculated Load. This value is 15% of the NEC calculated load value. This value must not exceed the inverter max continuous output power rating.
(7) | The Battery Module Model is chosen from the drop down list of certified battery modules compatible for use. These battery modules are to be ordered using Generac SKUs (via a Generac distributor) as only specific models of these modules are recognized components of the Generac PWRcell Battery.
(8) | The Battery Module Quantity is the count of battery modules expected to be populated in PWRcell Battery/ies to support the backup of dwelling loads during power outages. The total value range is between 3 to 12 modules. This is to account for between 3 to 6 modules per PWRcell Battery and with up to two PWRcell Batteries connected to one PWRcell Inverter. Up to two PWRcell Batteries are commonly attached to the inverter in practical applications that also include solar/PV.
(9) | The Estimated Backup Duration is the time, in hours, the PWRcell system is expected to support the dwelling loads. This value assumes that the continuous load is 20% of the NEC calculated load and the PWRcell Battery/ies is/are at 100% state of charge (SoC) at the start of the outage. This value is based on the NEC Calculated Load from Section 3 and the battery module model from Section 7, and battery module quantity from Section 7.

## Whole Home Sizing Worksheet
|  | Whole Home Sizing Worksheet NEC Article 220 Part III | [12 empty] | METADATA
Battery Module Capacity (kWh)
Contractor |  |  |  |  | E-mail | [10 empty] | Battery Modules Model | DCB | 3 | 2.85
Phone |  |  |  |  | Fax |  |  |  |  | WORKSHEET RESULTS |  |  | Value | Units |  |  | EX | 3
Job Name |  |  |  |  | Address |  |  |  |  | (3) Total NEC Calculated Load |  |  | 0 | kW
Service Size | [9 empty] | (7) Battery Module Model | [5 empty] | Selected Module
[10 empty] | (8) Battery Module Quantity |  |  |  | Modules |  | Managed Loads Values | YES | N/A
[10 empty] | (9) Estimated Backup Duration |  |  |  | Hours |  |  | NO
[17 empty] | LOCKOUT |  |  |  | Highlight Batt Mod Cells?
Load Description |  |  |  | Quantity (or Sq. Ft.) | Load Rating (VA) | Apparent Power (VA) | Managed Load?9 |  |  | Pre-populated values are BLACK.1 User-entered values are BLUE. NEC Section References are [PURPLE] | [5 empty] | PWRcell system Max Continuous Load |  |  |  |  | FALSE
(1) GENERAL LOADS
(1a) GENERAL LIGHTING LOADS | [14 empty] | Count | Load Name
General Lighting and Receptacles |  |  |  |  | 3 VA/Sq. Ft. | 0 |  |  |  | (4) MANAGED / LOCKED OUT LOADS9 |  |  |  | VA | 0 | General Lighting and Receptacles |  | 3 VA/Sq. Ft. |  | 0
Small Appliance Circuits |  |  |  |  | 1500 | 0 | [8 empty] | 0 | Small Appliance Circuits |  | 1500 |  | 0
Laundry Circuit |  |  |  |  | 1500 | 0 | [8 empty] | 0 | Laundry Circuit |  | 1500 |  | 0
|  |  | TOTAL UNMANAGED LIGHTING LOAD |  |  | 0 | VA
| (1b) [TABLE 220.42] ADJUSTED TOTAL LIGHTING LOAD |  |  |  |  | 0 | VA
(1c) FIXED APPLIANCES1
Dishwasher |  |  |  |  | 1500 | 0 | [8 empty] | 0 | Dishwasher |  | 1500 |  | 0
Garbage Disposal |  |  |  |  | 800 | 0 | [8 empty] | 0 | Garbage Disposal |  | 800 |  | 0
Forced Air Furnace (Oil/NG/LP) |  |  |  |  | 600 | 0 | [8 empty] | 0 | Forced Air Furnace (Oil/NG/LP) |  | 600 |  | 0
Microwave Range Hood |  |  |  |  | 1600 | 0 | [8 empty] | 0 | Microwave Range Hood |  | 1600 |  | 0 | Check Managed Load
Septic Grinder / Lift Pump |  |  |  |  | 850 | 0 | [8 empty] | 0 | Septic Grinder / Lift Pump |  | 850 |  | 0 | 0
Sump Pump |  |  |  |  | 750 | 0 | [8 empty] | 0 | Sump Pump |  | 750 |  | 0
Water Heater - Electric (240V) |  |  |  |  | 4500 | 0 | [8 empty] | 0 | Water Heater - Electric (240V) |  | 4500 |  | 0
Well Pump (1/2 HP) |  |  |  |  | 1200 | 0 | [8 empty] | 0 | Well Pump (1/2 HP) |  | 1200 |  | 0
Well Pump (3/4 HP) |  |  |  |  | 1750 | 0 | [8 empty] | 0 | Well Pump (3/4 HP) |  | 1750 |  | 0
Well Pump (1 HP) |  |  |  |  | 2350 | 0 | [8 empty] | 0 | Well Pump (1 HP) |  | 2350 |  | 0
(1d) OTHER FIXED APPLIANCES1
Compressor |  |  |  |  | 2000 | 0 | [8 empty] | 0 | Compressor |  | 2000 |  | 0
Hot Tub |  |  |  |  | 10000 | 0 | [8 empty] | 0 | Hot Tub |  | 10000 |  | 0
Sauna |  |  |  |  | 5000 | 0 | [8 empty] | 0 | Sauna |  | 5000 |  | 0
Welder |  |  |  |  | 2000 | 0 | [8 empty] | 0 | Welder |  | 2000 |  | 0
[15 empty] | 0 | 0
[15 empty] | 0 | 0
[15 empty] | 0 | 0
[15 empty] | 0 | 0
TOTAL UNMANAGED FIXED APPLIANCES |  |  |  | 0
| TOTAL UNMANAGED FIXED APPLIANCE LOAD |  |  |  |  | 0 | VA
(1e) [220.53] ADJUSTED TOTAL FIXED APPLIANCE LOAD | [5 empty] | 0 | VA |  |  | TOTAL MANAGED LOAD |  |  |  | 0
(1f) SPECIFICALLY-ADJUSTED APPLIANCES
[220.54] Electric Clothes Dryer | [5 empty] | 0 | [8 empty] | 0 | Electric Clothes Dryer (240V) |  |  |  | 0
[220.55] Electric Cooking Appliances (240V) |  |  |  |  | < 120003 | 0 |  |  | NOTE: Use the Actual Nameplate LRA area below to check the LRA rating of the load with highest LRA. Please consider baseload (unmanaged loads) when determining feasibliity of starting LRA based on these results. | [5 empty] | 0 | Electric Cooking Equipment (240V) |  | < 120003 |  | 0
TOTAL UNMANAGED SPECIFICALLY-ADJUSTED APPLIANCES LOAD | [5 empty] | 0 | VA
(2) HEAT AND A/C LOADS
(2a) A/C COOLING & HEAT PUMPS1,2 | [7 empty] | (5) | Locked Rotor Amps8 |  |  | With Soft Starter8
1 Ton (typ. FLA 5) |  |  |  |  | 1000 | 0 |  | ↔ | 33 |  | Amps | 13.2 |  | Amps | 0 | 1 Ton A/C & Heat Pumps |  | 1000 |  | 0
2 Ton (typ. FLA 10) |  |  |  |  | 2000 | 0 |  | ↔ | 67 |  | Amps | 26.8 |  | Amps | 0 | 2 Ton A/C & Heat Pumps |  | 2000 |  | 0
3 Ton (typ. FLA 15) |  |  |  |  | 3000 | 0 |  | ↔ | 100 |  | Amps | 40 |  | Amps | 0 | 3 Ton A/C & Heat Pumps |  | 3000 |  | 0
4 Ton (typ. FLA 20) |  |  |  |  | 4000 | 0 |  | ↔ | 117 |  | Amps | 46.8 |  | Amps | 0 | 4 Ton A/C & Heat Pumps |  | 4000 |  | 0
5 Ton (typ. FLA 25) |  |  |  |  | 5000 | 0 |  | ↔ | 145 |  | Amps | 58 |  | Amps | 0 | 5 Ton A/C & Heat Pumps |  | 5000 |  | 0
(2b) SUPPLEMENTAL ELECTRIC HEAT | [8 empty] | Actual Nameplate LRA |  |  | With Soft Starter
Supplemental Heat Strips4 |  |  |  |  | 5000 | 0 |  |  |  |  | Amps | 0 |  | Amps | 0 | Supplemental Electric Heat |  | 5000 |  | 0
(2c) FIXED ELECTRIC SPACE HEATING |  |  |  | Total Feet
Baseboard Heaters5 |  |  |  |  | 250 | 0 | [8 empty] | 0 | Fixed Electric Space Heating |  | 250 |  | 0
| TOTAL UNMANAGED HEAT AND A/C LOADS |  |  |  |  | 0 | VA
(3) NEC CALCULATED LOAD | [5 empty] | Value
(1b) [TABLE 220.42] ADJUSTED TOTAL LIGHTING LOAD | [5 empty] | 0 | VA
(1e) [220.53] ADJUSTED TOTAL FIXED APPLIANCE LOAD | [5 empty] | 0 | VA
TOTAL UNMANAGED SPECIFICALLY-ADJUSTED APPLIANCES LOAD | [5 empty] | 0 | VA |  | NOTE: The phase imbalance seen on the inverter while supporting loads during an outage is not to exceed 30%. Please design load schedule accordingly.
|  | TOTAL UNMANAGED HEAT AND A/C LOAD |  |  |  | 0 | VA
|  | TOTAL NEC CALCULATED LOAD6 |  |  |  | 0 | kW
|  |  |  | (4) TOTAL MANAGED LOAD6 |  | 0 | kW
1Initial values for loads in this section are estimates; verify nameplate data for accurate results
2If multiple units are present on site, account for all units
3Calculations derived using NEC Table 220.55, Column C. Individual nameplate ratings must not exceed than 12000 VA. See Section (1f) instructions for more information
4Quantity value is kVA in increments of 5 kVA. Quantity = Total kVA / 5 kVA
5Fixed Electric Heating is typically estimated at 250 watts per foot, enter total distance in feet.
6Power value (in kW) is calculated as VA / 1000 W, where it is assumed that PF = 1.
7Peak motor starrting current may not be achieveable at reduced PWRcell Battery State of Charge
8Assumes a 6 module PWRcell Battery.
9Load Management of 120 V loads requires management of the subpanel where the 120 V loads are terminated.
LRA Numbers in Green can be started by the ESS8
LRA Numbers in Orange may/may not be started by the ESS7,8
LRA Numbers in Red cannot be started by the ESS
ESS Max Motor Starting Capability: 50 A7

## Change Log (hidden)
Change Log after… | Version 1.1.1
Area | Change Description (Short) | Change Desciption (Detailed) | Change Impact
ESS Whole Home Sizing sheet | Cosmetic revisions | Revise backfill transparency for color-filled cells in LRA table area. Label and emphasize worksheet outputs/results. Revise color-coding of "total managed load" text from red to black. | Minor/Bug
ESS Whole Home Sizing sheet | Cosmetic revisions (cont'd) | Revised font and size of LRA Numbers text box. Revised title to remove word "Residential". | Minor/Bug
ESS Whole Home Sizing sheet | Logic Improvements | Updated results section logic to check that battery module model and quantity have been provided before providing a result. If NEC calculated load is greater than capacity, the cell will display text "TOO HIGH". | Minor/Bug
User Guide - READ ME | Terminology revision | Revised instances of PWRcell ESS that should be PWRcell Battery, PWRcell Batteries, or PWRcell Battery/ies in Read Me sections 7, 8, and 9. | Minor/Bug
User Guide - READ ME | Instruction Update for Logic improvements | Revised instructions for Section 3 based on logic changes for Section 3 cell value. | Minor/Bug
Both sheets | Revised label for Section 9 | Revised Section 9 label from "Estimated ESS Duration" to "Estimated Backup Duration". | Minor/Bug
Overal Milestone Impact: | Minor/Bug
Next Production Version: | Version 1.1.2